## Sheet1
Extended UDT | Ignition Name | Data Type | Atomic Type | Sample UDT Instance Name | Sample PLC Tag | Template Strategy | Parameter 1 | Parameter 2 | Parameter 3 | Parameter 4 | Overwrite Option
ALLEN_BRADLEY/PIG_LAUNCHER_CLX | CURRENT_HOUR | i2 | extension | 01_20_HUDSON | AUTO_LAUNCH_HOURS<I1>
ALLEN_BRADLEY/PIG_LAUNCHER_CLX | CURRENT_MINUTE | i2 | extension | 01_20_HUDSON | AUTO_LAUNCH_MINUTES<I1>
ALLEN_BRADLEY/PIG_LAUNCHER_CLX | TIMER | i2 | extension | 01_20_HUDSON | LAUNCH_TIMER_HOURS_HMI<I1>
ALLEN_BRADLEY/PIG_LAUNCHER_CLX | EMPTY_BARREL | r4 | extension | 01_20_HUDSON | NO_PIGS_AD.InAlarm<I1>
ALLEN_BRADLEY/PIG_LAUNCHER_CLX | ESD_SHUTDOWN | boolean | extension | 01_20_HUDSON | MESD_1_AD.InAlarm<I1>
ALLEN_BRADLEY/PIG_LAUNCHER_CLX | NUM_PIGS_IN_BARREL_SP | i2 | extension | 01_20_HUDSON | PIG_COUNT<I1>
ALLEN_BRADLEY/PIG_LAUNCHER_CLX | AUTO_MAN | boolean | extension | 01_20_HUDSON | HMI_AUTO<I1>
ALLEN_BRADLEY/PIG_LAUNCHER_CLX | RESET | boolean | extension | 01_20_HUDSON | HMI_RESET<I1>
ALLEN_BRADLEY/PIG_LAUNCHER_CLX | LAUNCH_FAIL | r4 | extension | 01_20_HUDSON | FAILED_LAUNCH_AD.InAlarm<I1>
ALLEN_BRADLEY/PIG_LAUNCHER_CLX | FLOW_INHIBIT_STATUS | boolean | extension | 01_20_HUDSON | PIG_INHIBIT<I1>
ALLEN_BRADLEY/PIG_LAUNCHER_CLX | NUM_PIGS_REMAINING | i2 | extension | 01_20_HUDSON | PIGS_LAUNCHED<I1>
ALLEN_BRADLEY/PIG_LAUNCHER_CLX | PERMISSIVE | r4 | extension | 01_20_HUDSON | LAUNCHING<I1>
ALLEN_BRADLEY/PIG_LAUNCHER_CLX | STATUS | r4 | extension | 01_20_HUDSON | LAUNCH_READY<I1>
ALLEN_BRADLEY/PIG_LAUNCHER_CLX | VALVE_POSITION | r4 | extension | 01_20_HUDSON | PADDLE_POSITION<I1>
ALLEN_BRADLEY/PIG_LAUNCHER_CLX | INHIBIT | boolean | extension | 01_20_WATTENBERG | SCADA_LOCKOUT<I1>
ALLEN_BRADLEY/PIG_LAUNCHER_CLX | VALVE_STATUS | i2 | extension | 16_19_1410_24WELDFIT | WEST_VALVE_POSITION<I1>
EMERSONROCL/DEVICE_STD | BATTERY_VOLTAGE | FLP | extension | A09G59 | 52.1.1<TFLP><I1>
EMERSONROCL/DEVICE_STD | CURRENT_HOUR | UINT 8 | extension | A09G59 | 12.2.1<TUINT8><I1>
EMERSONROCL/DEVICE_STD | CURRENT_MINUTE | UINT 8 | extension | A09G59 | 12.1.1<TUINT8><I1>
EMERSONROCL/DEVICE_STD | RTU_BOARD_TEMPERATURE | FLP | extension | A09G59 | 52.3.1<TFLP><I1>
EMERSONROCL/DEVICE_STD | AIR_SUPPLY_PRESSURE_ALARM | r4 | extension | A10G32 | 98.1.3<TBIN><I1>
EMERSONROCL/DEVICE_STD | OIL_TEMP_ALARM | r4 | extension | A10G32 | 98.2.3<TBIN><I1>
EMERSONROCL/DEVICE_STD | PIPELINE_PRESSURE_ALARM | r4 | extension | A10G32 | 98.3.3<TBIN><I1>
EMERSONROCL/DEVICE_STD | MEASUREMENT_SKID_SUMP | r4 | extension | A10G32 | 98.4.3<TBIN><I1>
EMERSONROCL/DEVICE_STD | PRODUCTION_PERMISSIVE | r4 | extension | A10G32 | 98.5.3<TBIN><I1>
EMERSONROCL/DEVICE_STD | ROC_LOW_VOLTAGE_ALARM | r4 | extension | A10G32 | 98.6.3<TBIN><I1>
EMERSONROCL/DEVICE_STD | NO_FLOW_ALARM | r4 | extension | A10G32 | 98.7.3<TBIN><I1>
EMERSONROCL/DEVICE_STD | OIL_DENSITY_ALARM | r4 | extension | A10G32 | 98.8.3<TBIN><I1>
EMERSONROCL/DEVICE_STD | DRIVE_GAIN_ALARM | r4 | extension | A10G32 | 98.9.3<TBIN><I1>
EMERSONROCL/DEVICE_STD | BACK_PRESSURE_ALARM | r4 | extension | A10G32 | 98.10.3<TBIN><I1>
EMERSONROCL/DEVICE_STD | COMM_FAIL_TO_RTU | r4 | extension | A10G32 | 98.11.3<TBIN><I1>
EMERSONROCL/DEVICE_STD | ESD_VALVE_NORMALLY_OPEN | r4 | extension | A10G32 | 98.12.3<TBIN><I1>
EMERSONROCL/DEVICE_STD | ESD_VALVE_NORMALLY_CLOSED | r4 | extension | A10G32 | 98.13.3<TBIN><I1>
EMERSONROCL/DEVICE_STD | BSW_ACCUM_ALARM | r4 | extension | A10G32 | 98.14.3<TBIN><I1>
EMERSONROCL/DEVICE_STD | RTU_BOARD_TEMPERATURE | r4 | extension | A207G45 | 109.12.5<TFLP><I1>
EMERSONROCL/METER_GAS_STD | RATE | FLP | extension | A09G59 | 10.3.1<TFLP><I1>
EMERSONROCL/METER_GAS_STD | ENERGY | FLP | extension | A09G59 | 10.4.1<TFLP><I1>
EMERSONROCL/METER_GAS_STD | ENERGY_TODAY | FLP | extension | A09G59 | 10.6.1<TFLP><I1>
EMERSONROCL/METER_GAS_STD | ENERGY_YESTERDAY | FLP | extension | A09G59 | 10.8.1<TFLP><I1>
EMERSONROCL/METER_GAS_STD | VOLUME_TODAY | FLP | extension | A09G59 | 10.5.1<TFLP><I1>
EMERSONROCL/METER_GAS_STD | VOLUME_YESTERDAY | FLP | extension | A09G59 | 10.7.1<TFLP><I1>
EMERSONROCL/METER_GAS_STD | DIFFERENTIAL_PRESSURE | FLP | extension | A09G59 | 10.0.1<TFLP><I1>
EMERSONROCL/METER_GAS_STD | STATIC_PRESSURE | FLP | extension | A09G59 | 10.1.1<TFLP><I1>
EMERSONROCL/METER_GAS_STD | TEMPERATURE | FLP | extension | A09G59 | 10.2.1<TFLP><I1>
EMERSONROCL/METER_GAS_STD | RATE | r4 | extension | A100G45 | 116.0.2<TFLP><I1>
EMERSONROCL/METER_GAS_STD | ENERGY_TODAY | r4 | extension | A100G45 | 116.22.2<TFLP><I1>
EMERSONROCL/METER_GAS_STD | ENERGY_YESTERDAY | r4 | extension | A100G45 | 116.23.2<TFLP><I1>
EMERSONROCL/METER_GAS_STD | VOLUME_TODAY | r4 | extension | A100G45 | 116.12.2<TFLP><I1>
EMERSONROCL/METER_GAS_STD | VOLUME_YESTERDAY | r4 | extension | A100G45 | 116.13.2<TFLP><I1>
EMERSONROCL/METER_GAS_STD | STATIC_PRESSURE | ui1 | extension | A100G45 | 115.2.2<TFLP><I1>
EMERSONROCL/METER_GAS_STD | TEMPERATURE | r4 | extension | A100G45 | 115.18.2<TFLP><I1>
EMERSONROCL/METER_GAS_STD | VOLTAGE | FLP | extension | A100G46 | 3.14.66<TFLP><I1>
EMERSONROCL/METER_GAS_STD | CURRENT_HOUR | UINT 8 | extension | A100G46 | 12.2.1<TUINT8><I1>
EMERSONROCL/METER_GAS_STD | CURRENT_MINUTE | UINT 8 | extension | A101G54 | 12.1.1<TUINT8><I1>
EMERSONROCL/METER_GAS_STD | STATIC_PRESSURE | r4 | extension | A104G45 | 115.16.2<TFLP><I1>
EMERSONROCL/METER_GAS_STD | ENERGY | r4 | extension | A108G45 | 112.54.2<TFLP><I1>
EMERSONROCL/METER_GAS_STD | CONDENSATE_VOLUME_MONTH | r8 | extension | A110G45 | 204.135.2<TFLP><I1>
EMERSONROCL/METER_GAS_STD | CONDENSATE_VOLUME_MONTHP | r8 | extension | A110G45 | 204.141.2<TFLP><I1>
EMERSONROCL/METER_GAS_STD | CONDENSATE_VOLUME_YESTERDAY | r8 | extension | A110G45 | 204.129.2<TFLP><I1>
EMERSONROCL/METER_GAS_STD | STATIC_PRESSURE | r8 | extension | A110G45 | 204.33.2<TFLP><I1>
EMERSONROCL/METER_GAS_STD | VOLUMETRIC_FLOW_RATE_SETPOINT | r4 | extension | A117G45 | 110.11.2<TFLP><I1>
EMERSONROCL/METER_GAS_STD | VALVE_POSITION | r4 | extension | A117G45 | 110.37.2<TFLP><I1>
EMERSONROCL/METER_GAS_STD | BTU | r4 | extension | A182G45 | 112.22.2<TFLP><I1>
EMERSONROCL/METER_OIL_ALARM | RESET_BSW_OVER_RANGE_ALARM | FLP 32 | extension | A100G32_ALARM | 98.14.2<TBIN><I1>
EMERSONROCL/METER_OIL_ALARM | CURRENT_AIR_PSI | FLP 32 | extension | A100G32_ALARM | 103.21.41<TFLP><I1>
EMERSONROCL/METER_OIL_ALARM | CURRENT_OIL_TEMP | FLP 32 | extension | A100G32_ALARM | 103.21.34<TFLP><I1>
EMERSONROCL/METER_OIL_ALARM | CURRENT_PIPELINE_PSI | FLP 32 | extension | A100G32_ALARM | 103.21.36<TFLP><I1>
EMERSONROCL/METER_OIL_ALARM | CURRENT_FLOW_RATE | FLP 64 | extension | A100G32_ALARM | 204.105.1<TFLP><I1>
EMERSONROCL/METER_OIL_ALARM | SUMP_SWITCH | UINT 8 | extension | A100G32_ALARM | 101.15.59<TBIN><I1>
EMERSONROCL/METER_OIL_ALARM | CURRENT_ROC_VOLTAGE | FLP 32 | extension | A100G32_ALARM | 109.12.2<TFLP><I1>
EMERSONROCL/METER_OIL_ALARM | CURRENT_HEARTBEAT | FLP 32 | extension | A100G32_ALARM | 98.3.8<TFLP><I1>
EMERSONROCL/METER_OIL_ALARM | ESD_VALVE_STATUS | UINT 8 | extension | A100G32_ALARM | 102.8.65<TBIN><I1>
EMERSONROCL/METER_OIL_ALARM | MEASUREMENT_PERMISSIVE | UINT 8 | extension | A100G32_ALARM | 102.8.68<TBIN><I1>
EMERSONROCL/METER_OIL_ALARM | WES_IOC_LOTO_PERMISSIVE | FLP 32 | extension | A100G32_ALARM | 98.1.1<TBIN><I1>
EMERSONROCL/METER_OIL_ALARM | ESD_VALVE_CURRENT_STATE | UINT 8 | extension | A100G32_ALARM | 101.3.57<TBIN><I1>
EMERSONROCL/METER_OIL_ALARM | LIVE_BSW_READING_MAIN | FLP 32 | extension | A100G32_ALARM | 103.21.35<TFLP><I1>
EMERSONROCL/METER_OIL_ALARM | LIVE_DENSITY_READING | FLP 64 | extension | A100G32_ALARM | 202.13.1<TFLP><I1>
EMERSONROCL/METER_OIL_ALARM | PRODUCTION_PERMISSIVE | UINT 8 | extension | A100G32_ALARM | 101.3.63<TBIN><I1>
EMERSONROCL/METER_OIL_ALARM | MAIN_LACT_RUN_STATUS | FLP 32 | extension | A100G32_ALARM | 98.1.3<TBIN><I1>
EMERSONROCL/METER_OIL_ALARM | CORIOLIS_PRESSURE | FLP 32 | extension | A100G32_ALARM | 103.21.33<TFLP><I1>
EMERSONROCL/METER_OIL_ALARM | DIVERT_VALVE_STATUS | FLP 32 | extension | A100G32_ALARM | 98.1.3<TBIN><I1>
EMERSONROCL/METER_OIL_ALARM | PROD_MAIN_LACT_BSW | FLP 32 | extension | A100G32_ALARM | 103.21.35<TFLP><I1>
EMERSONROCL/METER_OIL_ALARM | CYGNET_DISPLAY_TLP | FLP 32 | extension | A100G32_ALARM | 98.20.1<TFLP><I1>
EMERSONROCL/METER_OIL_ALARM | BULK_TANK_PRESSURE | FLP 32 | extension | A100G32_ALARM | 98.1.8<TFLP><I1>
EMERSONROCL/METER_OIL_ALARM | CURRENT_DRIVE_GAIN | FLP 32 | extension | A100G32_ALARM | 98.6.7<TFLP><I1>
EMERSONROCL/METER_OIL_ALARM | BSW_TOTAL | FLP 32 | extension | A100G32_ALARM | 96.3.2<TFLP><I1>
EMERSONROCL/METER_OIL_STD | DRIVE_GAIN | FLP | extension | A100G32 | 98.6.7<TFLP><I1>
EMERSONROCL/METER_OIL_STD | VOLTAGE | FLP | extension | A100G32 | 109.12.2<TFLP><I1>
EMERSONROCL/METER_OIL_STD | RATE | r8 | extension | A100G32 | 204.106.2<TFLP><I1>
EMERSONROCL/METER_OIL_STD | DENSITY | r8 | extension | A100G32 | 204.21.2<TFLP><I1>
EMERSONROCL/METER_OIL_STD | RATE_GSV | r8 | extension | A100G32 | 204.105.2<TFLP><I1>
EMERSONROCL/METER_OIL_STD | VOLUME_MONTH_GSV | r8 | extension | A100G32 | 204.135.2<TFLP><I1>
EMERSONROCL/METER_OIL_STD | VOLUME_MONTHP_GSV | r8 | extension | A100G32 | 204.141.2<TFLP><I1>
EMERSONROCL/METER_OIL_STD | VOLUME_YESTERDAY_GSV | r8 | extension | A100G32 | 204.129.2<TFLP><I1>
EMERSONROCL/METER_OIL_STD | VOLUME_MONTH | r8 | extension | A100G32 | 204.136.2<TFLP><I1>
EMERSONROCL/METER_OIL_STD | VOLUME_MONTHP | r8 | extension | A100G32 | 204.142.2<TFLP><I1>
EMERSONROCL/METER_OIL_STD | VOLUME_TODAY | r8 | extension | A100G32 | 204.124.2<TFLP><I1>
EMERSONROCL/METER_OIL_STD | VOLUME_YESTERDAY | r8 | extension | A100G32 | 204.130.2<TFLP><I1>
EMERSONROCL/METER_OIL_STD | INSTRUMENT_AIR | FLP | extension | A100G32 | 103.21.41<TFLP><I1>
EMERSONROCL/METER_OIL_STD | DISCHARGE_PRESSURE | FLP | extension | A100G32 | 103.21.36<TFLP><I1>
EMERSONROCL/METER_OIL_STD | PRESSURE | r8 | extension | A100G32 | 204.33.2<TFLP><I1>
EMERSONROCL/METER_OIL_STD | SUCTION_PRESSURE | FLP | extension | A100G32 | 98.1.8<TFLP><I1>
EMERSONROCL/METER_OIL_STD | SAMPLER_VOLUME | FLP | extension | A100G32 | 98.5.30<TFLP><I1>
EMERSONROCL/METER_OIL_STD | TEMPERATURE | r8 | extension | A100G32 | 204.34.2<TFLP><I1>
EMERSONROCL/METER_OIL_STD | PERMISSIVE | UINT 8 | extension | A100G32 | 101.3.63<TBIN><I1>
EMERSONROCL/METER_OIL_STD | VALVE_POSITION | UINT 8 | extension | A100G32 | 101.3.57<TFLP><I1>
EMERSONROCL/METER_OIL_STD | NGL_RATE | r8 | extension | A102G45 | 204.105.2<TFLP><I1>
EMERSONROCL/METER_OIL_STD | CONDENSATE_VOLUME_MONTH | r8 | extension | A110G32 | 204.135.2<TFLP><I1>
EMERSONROCL/METER_OIL_STD | CONDENSATE_VOLUME_YESTERDAY | r8 | extension | A110G32 | 204.129.2<TFLP><I1>
EMERSONROCL/METER_OIL_STD | VOLUMETRIC_FLOW_RATE_SETPOINT | r4 | extension | A111G32 | 110.11.2<TFLP><I1>
EMERSONROCL/METER_OIL_STD | PID_MODE | ui1 | extension | A111G32 | 110.22.2<TBIN><I1>
EMERSONROCL/METER_OIL_STD | VALVE_POSITION | r4 | extension | A111G32 | 110.37.2<TFLP><I1>
EMERSONROCL/METER_OIL_STD | MASS_RATE | r8 | extension | A111G32 | 204.108.5<TFLP><I1>
EMERSONROCL/METER_OIL_STD | ACCUMULATOR_OIL | r8 | extension | A111G32 | 204.148.5<TFLP><I1>
EMERSONROCL/METER_OIL_STD | PID_CV_READ | r4 | extension | A111G32 | 110.37.4<TFLP><I1>
EMERSONROCL/METER_OIL_STD | PID_TARGET_SP_PRIMARY | r4 | extension | A111G32 | 110.11.4<TFLP><I1>
EMERSONROCL/METER_OIL_STD | CONDENSATE_RATE | r8 | extension | A128G45 | 204.105.2<TFLP><I1>
EMERSONROCL/METER_OIL_STD | CONDENSATE_VOLUME_MONTHP | r8 | extension | A165G45 | 204.141.2<TFLP><I1>
EMERSONROCL/METER_OIL_STD | STATIC_PRESSURE | r8 | extension | A178G45 | 204.33.2<TFLP><I1>
EMERSONROCL/METER_OIL_STD | FLOWING_GAS_TEMPERATURE | r8 | extension | A178G45 | 204.34.2<TFLP><I1>
EMERSONROCL/METER_OIL_SAMPLER | DESIRED_YZ_SAMPLER_FILL | FLP | extension | A100G32_SAMPLER | 98.11.30<TFLP><I1>
EMERSONROCL/METER_OIL_SAMPLER | BARRELS_PER_DAY | FLP | extension | A100G32_SAMPLER | 98.16.30<TFLP><I1>
EMERSONROCL/METER_OIL_SAMPLER | NUM_SAMPLING_DAYS_IN_MONTH | FLP | extension | A100G32_SAMPLER | 98.12.30<TUINT8><I1>
EMERSONROCL/METER_OIL_SAMPLER | BITE_SIZE_PER_PULSE | FLP | extension | A100G32_SAMPLER | 98.3.30<TFLP><I1>
EMERSONROCL/METER_OIL_SAMPLER | SAMPLE_BITE_DURATION | FLP | extension | A100G32_SAMPLER | 111.5.1<TFLP><I1>
EMERSONROCL/METER_OIL_SAMPLER | REQUIRED_CC_PER_DAY | FLP | extension | A100G32_SAMPLER | 98.13.30<TFLP><I1>
EMERSONROCL/METER_OIL_SAMPLER | PUMP_STROKES_PER_DAY | FLP | extension | A100G32_SAMPLER | 98.14.30<TFLP><I1>
EMERSONROCL/METER_OIL_SAMPLER | SAMPLE_BITE_FREQUENCY | FLP | extension | A100G32_SAMPLER | 111.4.1<TFLP><I1>
EMERSONROCL/METER_OIL_SAMPLER | YZ_SAMPLER_N2_LEAK | FLP | extension | A100G32_SAMPLER | 98.9.30<TBIN><I1>
EMERSONROCL/METER_OIL_SAMPLER | YZ_SAMPLER_OVER_50 | FLP | extension | A100G32_SAMPLER | 98.7.30<TBIN><I1>
EMERSONROCL/METER_OIL_SAMPLER | YZ_SAMPLER_OVER_80 | FLP | extension | A100G32_SAMPLER | 98.8.30<TBIN><I1>
EMERSONROCL/METER_OIL_SAMPLER | YZ_SAMPLER_NOT_FILLING | FLP | extension | A100G32_SAMPLER | 98.6.30<TBIN><I1>
EMERSONROCL/METER_OIL_SAMPLER | YZ_N2_PSI_BELOW_PIPELINE_PSI | FLP | extension | A100G32_SAMPLER | 98.15.30<TBIN><I1>
EMERSONROCL/METER_OIL_SAMPLER | VOLUME_INFO_FULL_CC | FLP | extension | A100G32_SAMPLER | 98.5.30<TFLP><I1>
EMERSONROCL/METER_OIL_SAMPLER | VOLUME_INFO_PERCENT_FULL | FLP | extension | A100G32_SAMPLER | 98.4.30<TFLP><I1>
EMERSONROCL/METER_OIL_SAMPLER | VOLUME_INFO_BITE_SIZE | FLP | extension | A100G32_SAMPLER | 98.3.30<TFLP><I1>
EMERSONROCL/METER_OIL_SAMPLER | VOLUME_INFO_SAMPLE_RESET_BUTTON | FLP | extension | A100G32_SAMPLER | 98.1.30<TBIN><I1>
EMERSONROCL/METER_OIL_SAMPLER | TROUBLESHOOT_INFO_YZ_SAMPLER_ENABLED | UINT 8 | extension | A100G32_SAMPLER | 111.0.1<TBIN><I1>
EMERSONROCL/METER_OIL_SAMPLER | TROUBLESHOOT_INFO_NITROGEN_AND_CORIOLIS | FLP | extension | A100G32_SAMPLER | 98.10.30<TFLP><I1>
EMERSONROCL/METER_OIL_SAMPLER | PREV_MONTH_TOTAL | FLP 64 | extension | A100G32_SAMPLER | 204.141.1<TFLP><I1>
EMERSONROCL/METER_OIL_SAMPLER | YEST_TOTAL | FLP 64 | extension | A100G32_SAMPLER | 204.129.1<TFLP><I1>
EMERSONROCL/METER_OIL_SAMPLER | CURRENT_MONTH_TOTAL | FLP 64 | extension | A100G32_SAMPLER | 204.135.1<TFLP><I1>
EMERSONROCL/METER_OIL_SAMPLER | CURRENT_FLOW_RATE | FLP 64 | extension | A100G32_SAMPLER | 204.105.1<TFLP><I1>
EMERSONROCL/METER_OIL_SAMPLER | TROUBLESHOOT_INFO_YZ_SAMPLER_ENABLED | FLP | extension | A111G46_SAMPLER | 111.0.1<TBIN><I1>
EMERSONROCL/METER_OIL_SAMPLER | TROUBLESHOOT_INFO_YZ_SAMPLER_DISABLED | FLP | extension | A111G46_SAMPLER | 111.0.1<TBIN><I1>
EMERSONROCL/METER_O2 | VOLUME_YESTERDAY | FLP | extension | A100G55 | 10.7.1<TFLP><I1>
EMERSONROCL/METER_O2 | VOLUME_YESTERDAY | r4 | extension | A207G45 | 116.13.2<TFLP><I1>
EMERSONROCL/METER_O2 | O2_PPM | r4 | extension | A212G45 | 103.21.33<TFLP><I1>
EMERSONROCL/VALVE | REVERSE_FLOW | FLP 32 | extension | A100G55 | 17.15.1<TFLP><I1>
EMERSONROCL/VALVE | VOLTAGE | FLP 32 | extension | A100G55 | 17.3.2<TFLP><I1>
EMERSONROCL/VALVE | VALVE_STATUS | r4 | extension | A209G45 | 110.37.2<TUINT8><I1>
EMERSONROCL/VALVE | VALVE_STATUS | ui1 | extension | A212G45 | 102.8.81<TUINT8><I1>
EMERSONROCL/ANALYSIS_STD | BTU | r4 | extension | A108G45 | 112.22.2<TFLP><I1>
EMERSONROCL/ANALYSIS_STD | METHANE | r4 | extension | A108G45 | 112.28.2<TFLP><I1>
EMERSONROCL/ANALYSIS_STD | ETHANE | r4 | extension | A108G45 | 112.29.2<TFLP><I1>
EMERSONROCL/ANALYSIS_STD | PROPANE | r4 | extension | A108G45 | 112.30.2<TFLP><I1>
EMERSONROCL/ANALYSIS_STD | HEXANE | r4 | extension | A108G45 | 112.35.2<TFLP><I1>
EMERSONROCL/ANALYSIS_STD | CARBON_DIOXIDE | r4 | extension | A108G45 | 112.27.2<TFLP><I1>
EMERSONROCL/ANALYSIS_STD | ISO_BUTANE | r4 | extension | A108G45 | 112.32.2<TFLP><I1>
EMERSONROCL/ANALYSIS_STD | ISO_PENTANE | r4 | extension | A108G45 | 112.34.2<TFLP><I1>
EMERSONROCL/ANALYSIS_STD | NITROGEN | r4 | extension | A108G45 | 112.26.2<TFLP><I1>
EMERSONROCL/ANALYSIS_STD | BUTANE | r4 | extension | A108G45 | 112.31.2<TFLP><I1>
EMERSONROCL/ANALYSIS_STD | PENTANE | r4 | extension | A108G45 | 112.33.2<TFLP><I1>
EMERSONROCL/ANALYSIS_STD | SPECIFIC_GRAVITY | r4 | extension | A108G45 | 112.23.2<TFLP><I1>
MODBUS/ICHEM_SOLAR_CHEMICAL_INJECTION | VOLTAGE | r4 | extension | ALVIN_DECHANT | 47417<I1>
MODBUS/ICHEM_SOLAR_CHEMICAL_INJECTION | LEVEL_ALARM_HIGH_HIGH | boolean | extension | ALVIN_DECHANT | 22455<I1>
MODBUS/ICHEM_SOLAR_CHEMICAL_INJECTION | TANK_LEVEL | r4 | extension | ALVIN_DECHANT | 47416<I1>
MODBUS/ICHEM_SOLAR_CHEMICAL_INJECTION | PRESSURE | r4 | extension | ALVIN_DECHANT | 47414<I1>
MODBUS/ICHEM_SOLAR_CHEMICAL_INJECTION | TEMPERATURE_ALARM_LOW_LOW | boolean | extension | ALVIN_DECHANT | 22452<I1>
MODBUS/ICHEM_SOLAR_CHEMICAL_INJECTION | TEMPERATURE | r4 | extension | ALVIN_DECHANT | 47415<I1>
MODBUS/ICHEM_SOLAR_CHEMICAL_INJECTION | TEMPERATURE_ALARM_HIGH_HIGH | boolean | extension | VALLEY | 22453<I1>
TOTALFLOWG4/METER_GAS_STD | RATE | r4 | extension | T000003 | 4:7:19:R4<I1>
TOTALFLOWG4/METER_GAS_STD | ENERGY | r4 | extension | T000003 | 4:7:62:R4<I1>
TOTALFLOWG4/METER_GAS_STD | ENERGY_TODAY | r4 | extension | T000003 | 4:3:98:R4<I1>
TOTALFLOWG4/METER_GAS_STD | ENERGY_YESTERDAY | r4 | extension | T000003 | 4:3:97:R4<I1>
TOTALFLOWG4/METER_GAS_STD | VOLUME_TODAY | r4 | extension | T000003 | 4:7:22:R4<I1>
TOTALFLOWG4/METER_GAS_STD | VOLUME_YESTERDAY | r4 | extension | T000003 | 4:7:23:R4<I1>
TOTALFLOWG4/METER_GAS_STD | CURRENT_HOUR | i2 | extension | T000003 | 0:8:4:UI1<I1>
TOTALFLOWG4/METER_GAS_STD | CURRENT_MINUTE | i2 | extension | T000003 | 0:8:5:UI1<I1>
TOTALFLOWG4/METER_GAS_STD | DIFFERENTIAL_PRESSURE | r4 | extension | T000003 | 4:7:0:R4<I1>
TOTALFLOWG4/METER_GAS_STD | STATIC_PRESSURE | r4 | extension | T000003 | 4:3:0:R4<I1>
TOTALFLOWG4/METER_GAS_STD | TEMPERATURE | r4 | extension | T000003 | 4:3:3:R4<I1>
TOTALFLOWG4/VALVE | BATTERY_VOLTAGE | r4 | extension | FCV_1022_8_E_RD | 1:3:5:R4<I1>
TOTALFLOWG4/VALVE | BATTERY_LOW | ui1 | extension | FCV_1022_8_E_RD | 9:5:2:UI1<I1>
TOTALFLOWG4/VALVE | VALVE_FAIL_TO_CLOSE | ui1 | extension | FCV_1022_8_E_RD | 9:5:6:UI1<I1>
TOTALFLOWG4/VALVE | VALVE_FAIL_TO_OPEN | ui1 | extension | FCV_1022_8_E_RD | 9:5:7:UI1<I1>
TOTALFLOWG4/VALVE | STATUS | ui1 | extension | FCV_1022_8_E_RD | 9:5:3:UI1<I1>
TOTALFLOWG4/VALVE | VALVE_CLOSED | ui1 | extension | FCV_1022_8_E_RD | 9:5:5:UI1<I1>
TOTALFLOWG4/VALVE | VALVE_OPENED | ui1 | extension | FCV_1022_8_E_RD | 9:5:4:UI1<I1>
TOTALFLOWG4/VALVE | PRESSURE | r4 | extension | FCV_362_8_1_RD | 7:3:0:R4<I1>
TOTALFLOWG4/VALVE | VALVE_STATUS | ui1 | extension | T000631 | 7:2:5:UI1<I1>
TOTALFLOWG4/VALVE | VALVE_STATUS | i2 | extension | T001338 | 241:200:9:UI1<I1>
ALLEN_BRADLEY/PIG_LAUNCHER_DF1 | CURRENT_HOUR | i2 | extension | PIG_FREDRICK | N7:12<I1>
ALLEN_BRADLEY/PIG_LAUNCHER_DF1 | CURRENT_MINUTE | i2 | extension | PIG_FREDRICK | N7:13<I1>
ALLEN_BRADLEY/PIG_LAUNCHER_DF1 | TIMER | i2 | extension | PIG_FREDRICK | N7:0<I1>
ALLEN_BRADLEY/PIG_LAUNCHER_DF1 | LONG_TRIGGER_DOWN_ALARM | boolean | extension | PIG_FREDRICK | N7:6/0<I1>
ALLEN_BRADLEY/PIG_LAUNCHER_DF1 | LONG_TRIGGER_UP_ALARM | boolean | extension | PIG_FREDRICK | N7:6/1<I1>
ALLEN_BRADLEY/PIG_LAUNCHER_DF1 | NUM_PIGS_IN_BARREL_SP | i2 | extension | PIG_FREDRICK | N7:10<I1>
ALLEN_BRADLEY/PIG_LAUNCHER_DF1 | AUTO_MAN | boolean | extension | PIG_FREDRICK | N7:9/0<I1>
ALLEN_BRADLEY/PIG_LAUNCHER_DF1 | LAUNCHER_MODE | boolean | extension | PIG_FREDRICK | N7:9/1<I1>
ALLEN_BRADLEY/PIG_LAUNCHER_DF1 | NUM_PIGS_REMAINING | i2 | extension | PIG_FREDRICK | N7:8<I1>
ALLEN_BRADLEY/PIG_LAUNCHER_DF1 | PERMISSIVE | boolean | extension | PIG_FREDRICK | N7:14/0<I1>
ALLEN_BRADLEY/PIG_LAUNCHER_DF1 | EMPTY_BARREL_SHUTDOWN | boolean | extension | PIG_FREDRICK | N7:11/0<I1>
ALLEN_BRADLEY/PIG_LAUNCHER_DF1 | STATUS | i2 | extension | PIG_FREDRICK | N7:4<I1>
ALLEN_BRADLEY/PIG_LAUNCHER_DF1 | SHORT_TRIGGER_DOWN_ALARM | boolean | extension | PIG_HUDSON | N7:6/2<I1>
ALLEN_BRADLEY/PIG_LAUNCHER_DF1 | SHORT_TRIGGER_UP_ALARM | boolean | extension | PIG_HUDSON | N7:6/3<I1>
ALLEN_BRADLEY/PIG_LAUNCHER_DF1 | PIG_SIGNAL_ALARM | boolean | extension | PIG_HUDSON | N7:16/0<I1>
ALLEN_BRADLEY/PIG_LAUNCHER_DF1 | PIG_SIGNAL_COUNTER | i2 | extension | PIG_HUDSON | N7:17<I1>
TOTALFLOWG4/METER_O2 | O2_PPM | r4 | extension | T001044 | 1:243:0:R4<I1>
TOTALFLOWG4/METER_O2 | LIQUID_DETECTED | r4 | extension | T001338 | 9:0:13:UI1<I1>
TOTALFLOWG4/METER_O2 | PRESSURE | r4 | extension | T001338 | 241:201:5:R4<I1>
TOTALFLOWG4/METER_O2 | PERMISSIVE | r4 | extension | T001338 | 9:0:18:UI1<I1>